## 1207BWA
[5 empty] | SCRUBBER TURN ON Check Sheet |  |  |  | TURN ON DATE |  | 2023 년 01 월 20 일
[9 empty] | 고객사 |  | 온세미컨덕터코리아
[9 empty] | 고객사 담당자 |  | 김일남 부장님
MODEL |  |  |  |  | 1701HW | SERIAL NO | M006875 |  | MAT 담당자 |  | 양윤철
대분류 | 중분류 | 소분류 | 세분류 | No | 검사항목 | 검사 포인트 |  | SPEC | 측정치 | Alarm Value | 비정상시 조치 내용 | 조치 결과
Main Utility | 전기 | AC 전원 |  | 1 |  |  |  |  | 208.0 V
|  | DC 전원 |  | 2 |  |  |  |  | 24.02 V
| 기체 | Air |  | 3
|  | N2 |  | 4
| 액체 | Water |  | 5 |  |  |  |  | 60 Kpa
|  | PCW |  | 6
Pressure | 일반 Pressure | Exhaust Pressure |  | 7 |  |  |  | -20 mmH₂O 이하 | -80 mmH₂O
|  | Inlet Pressure #1 |  | 8 |  |  |  | -20 mmH₂O 이하 | -82 mmH₂O
|  | Inlet Pressure #2 |  | 9
|  | Inlet Pressure #3 |  | 10
|  | Inlet Pressure #4 |  | 11
|  | Cabinet Pressure |  | 12 |  |  |  | ' -10 mmH₂O 이하 | -13 mmH₂O
| 공급기체 Pressure | Sleeve Pressure |  | 13
|  | Burnning #1 Pressure |  | 14 |  |  |  | 40 ~ 180 Kpa | 170 Kpa
|  | Burnning #2 Pressure |  | 15 |  |  |  | 40 ~ 180 Kpa | 176 Kpa
|  | Burnning #3 Pressure |  | 16
|  | Burnning #4 Pressure |  | 17
|  | Puege Pressure |  | 18
| 공급액체 Pressure | Circulation Water Pressure |  | 19 |  |  |  | 80~120 Kpa | 106 Kpa
|  | PCW Pressure |  | 20
|  | Steam Water Pressure |  | 21
|  | Fog Water Pressure |  | 22 |  |  |  | 0.08 ~ 0.1 Mpa | 0.09 Mpa
Temp | Heat Chamber Temp | Heater Temp #1 |  | 23 |  |  |  | 600 ~ 800℃ | 750℃
|  | Heater Temp #2 |  | 24
|  | Heater Temp #3 |  | 25
|  | Heater Temp #4 |  | 26
|  | Chamber Temp |  | 27 |  |  |  | 400 ~ 800℃
|  | Chamber Top Temp |  | 28
|  | Chamber Bottom Temp |  | 29
|  | Reactor Chamber Temp |  | 30
| Wet Chamber Temp | Exhaust Temp |  | 31 |  |  |  | 60℃ 이하 | 19℃
|  | Wet Temp |  | 32 |  |  |  | 60℃ 이하 | 25℃
| 공급액체 Temp | Supply Water Temp |  | 33
|  | PCW Temp |  | 34
| 기타 Temp | Cabinet Temp |  | 35 |  |  |  | 90℃ 이하 | 30℃
|  | Elect Panel Temp |  | 36
유량 | 기체유량 | Heater 유량 |  | 37
|  | Sleeve 유량 |  | 38 |  |  |  | 80~120 ℓ/min | 80 ℓ/min
|  | Burnning #1 유량 |  | 39 |  |  |  | 400~600 ℓ/min | 600 ℓ/min
|  | Burnning #2 유량 |  | 40 |  |  |  | 400~600 ℓ/min | 600 ℓ/min
|  | Burnning #3 유량 |  | 41
|  | Burnning #4 유량 |  | 42
|  | Inlet Purge #1 유량 |  | 43 |  |  |  | 160~200 ℓ/min | 260 ℓ/min
|  | Inlet Purge #2 유량 |  | 44
|  | Inlet Pressure Purge #1 유량 |  | 45 |  |  |  | 1~3 ℓ/min | 1 ℓ/min
|  | Inlet Pressure Purge #2 유량 |  | 46
|  | Inlet Pressure Purge #3 유량 |  | 47
|  | Inlet Pressure Purge #4 유량 |  | 48
Torch N2 유량
Torch Flange 유량
|  | Staem 유량 |  | 49
|  | Fog #1 유량 |  | 50 |  |  |  | 30~50 ℓ/min | 30 ℓ/min
|  | Fog #2 유량 |  | 51 |  |  |  | 30~50 ℓ/min | 30 ℓ/min
|  | Fog #3 유량 |  | 52 |  |  |  | 30~50 ℓ/min | 30 ℓ/min
|  | Fog #4 유량 |  | 53 |  |  |  | 30~50 ℓ/min | 30 ℓ/min
|  | Cleaning #1 유량 |  | 54
|  | Cleaning #2 유량 |  | 55
|  | Cleaning #3 유량 |  | 56
|  | Cleaning #4 유량 |  | 57
|  | ICS Purge #1 유량 |  | 58
|  | ICS Purge #2 유량 |  | 59
|  | BCS Purge #1 유량 |  | 60
|  | BCS Purge #2 유량 |  | 61
| 액체유량 | Supply Water 유량 |  | 62 |  |  |  | 15 ~ 20 ℓ/min | 15 ℓ/min
|  | PCW 유량 |  | 63
|  | Steam Water 유량 |  | 64
|  | Fog Water #1 유량 |  | 65
|  | Fog Water #2 유량 |  | 66
|  | Fog Water #3 유량 |  | 67
|  | Fog Water #4 유량 |  | 68
구동계통 | Actuator Valve | Auto 3Way Valve |  | 69
|  | Supply Water Actuator Valve |  | 70 |  |  |  |  | Ok
|  | PCW Actuator Valve |  | 71
|  | Drain Actuator Valve |  | 72
|  | Circulation Back-up Actuator Valve |  | 73
|  | Steam Water Actuator Valve |  | 74
|  | Fog Water Actuator Valve |  | 75
| Pump | Circulation Pump #1 |  | 76
|  | Circulation Pump #2 |  | 77
|  | Drain Pump |  | 78
|  | 외부 Tank Supply Water Pump |  | 79
|  | 외부 Tank Drain Pump |  | 80
| Blower | Blower |  | 81 |  |  |  |  | Ok
| Cleaning System | ICS |  | 82
|  | BCS |  | 83
| Fan | Cabinet Fan |  | 84
|  | Elect Panel Fan |  | 85
기타 |  | Wiring |  | 86 |  |  |  |  | Ok
|  | Tubing |  | 87 |  |  |  |  | Ok
|  | Cleaning |  | 88 |  |  |  |  | Ok
|  | Water Leak |  | 89
|  | Smoke Detector |  | 90 |  |  |  |  | Ok
|  | EMO |  | 91 |  |  |  |  | Ok
|  | Interlock 연동 |  | 92 |  |  |  |  | Ok
|  | CMS 연동 |  | 93 |  |  |  |  | Ok
|  | 지진브라켓 |  | 94
|  | PLC Version |  | 95 |  |  |  |  | 4.0.5
|  | Touch Version |  | 96 |  |  |  |  | 4.0.4
|  | 시간정보 |  | 97 |  |  |  |  | 10:50 / 10:50
Level Sensor | Type | Magnetic |  | 98 |  |  |  |  | Ok
|  | Float |  | 99
|  | 전극봉 |  | 100
최종 판정 | [7 empty] | 판정 구분 | G : GOOD (양호) NG : NO GOOD (불량) |  | G
특이사항
N/A
N/A
N/A
N/A
N/A
N/A
N/A
N/A
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
N2
Air
60
60
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60
N/A
60